## Sheet1
盤名 | 保護功能/Meter | 保護電驛 | 數量 | AI | BI | BO | 通訊 | Remarks
RCP1052 | 50N/51N/21/21N/67/67N/86/87L | 7SL86 | 2 |  |  |  |  | Supply by SIEMENS
RCP 01 IN01 | 50N/51N/21/21N/67/67N/86/87L | 7SL86 | 2 |  |  |  |  | Supply by Hitach-ABB
| 86L | LOR7805G | 1 |  |  | 10a10b |  | Supply by Hitach-ABB
| Multi Meter | UMG 509PRO | 1 |  |  |  | TCP/IP, ModBus… | Supply by Hitach-ABB
RCP 05 F04 | 50/51/50N/51N/27/59/59V0/81H/81L | REF615_H | 1 | 4I (Io 1/5A) + 5U | 16BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 87T/51G | RET615 | 1 | 7I (Io 1/5A) + 6RTD + 2mA | 8BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 87B | REB670 | 1 |  | 32BI | 48BO | 2*LC+1 | Supply by Hitach-ABB
| 86B | LOR7810G | 1 |  |  | 20a20b |  | Supply by Hitach-ABB
| 86T | LOR7805G | 1 |  |  | 10a10b |  | Supply by Hitach-ABB
| Multi Meter | UMG 509PRO | 1 |  |  |  | TCP/IP, ModBus… | Supply by Hitach-ABB
RCP 02 F01 | 87T/51G | RET615 | 1 | 7I (Io 1/5A) + 6RTD + 2mA | 8BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 50/51/50N/51N | REF615_D | 1 | 4I (Io 1/5A) | 12BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 86T | LOR7805G | 1 |  |  | 10a10b |  | Supply by Hitach-ABB
| Multi Meter | UMG 509PRO | 1 |  |  |  | TCP/IP, ModBus… | Supply by Hitach-ABB
RCP 03 F02 | 87T/51G | RET615 | 1 | 7I (Io 1/5A) + 6RTD + 2mA | 8BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 50/51/50N/51N | REF615_D | 1 | 4I (Io 1/5A) | 12BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 86T | LOR7805G | 1 |  |  | 10a10b |  | Supply by Hitach-ABB
| Multi Meter | UMG 509PRO | 1 |  |  |  | TCP/IP, ModBus… | Supply by Hitach-ABB
RCP 04 F03 | 87T/51G | RET615 | 1 | 7I (Io 1/5A) + 6RTD + 2mA | 8BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 50/51/50N/51N | REF615_D | 1 | 4I (Io 1/5A) | 12BI | 10BO | 2*LC+1*RS485 | Supply by Hitach-ABB
| 86T | LOR7805G | 1 |  |  | 10a10b |  | Supply by Hitach-ABB
| Multi Meter | UMG 509PRO | 1 |  |  |  | TCP/IP, ModBus… | Supply by Hitach-ABB